## Overview
OVERVIEW |  | Data Center Air-Management Tool, Version 3, March 15, 2023
This tool was developed jointly by Lawrence Berkeley National Laboratory (LBNL) and ANCIS Incorporated for the US Department of Energy (DOE)
Copyright© 2023 The Regents of the University of California, operator of the Lawrence Berkeley National Laboratory. All Rights Reserved.
Rack Cooling Index (RCI) is a Registered Trademark and Return Temperature Index (RTI) is a Trademark of ANCIS Incorporated (www.ancis.us)
Worksheet | Description |  |  | What does this Tool do?
Air management in Data Centers is important for energy, thermal, and capacity management.
Overview | This Sheet: Provides an overview of the data flow and selection of units (I-P or SI). |  |  | Based on user input, the Tool provides air management recommendations (actions) and the
potential for reducing the supply airflow rate and increasing the supply air temperature
Step 1: AHU | User input: Air-handler unit (AHU) data for calculating metric RTI. |  |  | (both having an impact on energy use) without affecting the thermal equipment environment.
It estimates fan/chiller energy, energy costs, carbon emissions, and simple payback periods.
Step 2: Equip | User input: Electronic equipment data for calculating metric RTI. |  |  | This Tool is intended mainly for raised-floor cooling with hot/cold aisles.
Step 3: RCI | User input: Equipment intake temperatures for calculating metric RCI. |  |  | How is the Tool used?
First, the user fills in data and answers questions on the four input sheets (Steps 1-4). Each
Step 4: Main Input | User input: Main user input, including calculated metrics from Steps 1-3. |  |  | sheet includes basic guidance for entering the data correctly. Second, based on this user
input, numerical output and recommended actions are given on the two result output sheets
Step 5: Main Results | Result output: Main results but excluding energy estimates. |  |  | (Steps 5-6). User's Manual, Engineering Reference, and Data Collection Guide are available.
Step 6: Energy Results | Result output: Energy estimates for fans and chillers. |  |  | DOE Tool Suite
This Air Management Tool is part of a Tool Suite, which includes a Profiling Tool, an Electrical
Lookup | Lookup tables for internal use (hidden) |  |  | Tool, and an IT Equipment Tool. The individual tools are designed as "stand-alone" modules.
More information at http://datacenters.lbl.gov/tools
Action Rules | Rules for triggering actions or recommendations (hidden)
Questions, comments, and/or suggestions?
Export | Output for post-processing (hidden) |  |  | Please contact mherrlin@ancis.us
| Selection of Units |  | I-P
Selection of I-P or SI units will not change the
numerical values already entered into cells.
Computer must always use the U.S. number format,
i.e., decimal point (even when SI units are selected).

## Step 1 AHU
Step 1: AHU (AIR HANDLER UNITS)
| AHU | Supply Air | Return Air |  |  |  |  | By inserting the requested AHU data (yellow cells) for up to 40 operating
| Airflow | Temperature | Temperature | SATW | RATW | DTW |  | units, this spreadsheet will calculate four pieces of data (orange boxes)
| [cfm] or [m3/s] | [F] or [C] | [F] or [C] | [F] or [C] | [F] or [C] |  |  | and insert them on the Main Input (Step 4) sheet. It is imperative to
AHU 1 | 10000 | 65 | 75 | 21.6667 | 25 | N/A |  | enter (accurate) data on this sheet.
AHU 2 | 20000 | 65 | 80 | 43.3333 | 53.3333 | N/A
AHU 3 |  |  |  | 0 | 0 | N/A |  | The principal purpose of the data transfer is to help calculate the Return
AHU 4 |  |  |  | 0 | 0 | N/A |  | Temperature Index (RTI)TM on the Main Input sheet. This index plays
AHU 5 |  |  |  | 0 | 0 | N/A |  | an important role in understanding whether the data center is over-
AHU 6 |  |  |  | 0 | 0 | N/A |  | (by-pass) or under (recirculation) ventilated.
AHU 7 |  |  |  | 0 | 0 | N/A
AHU 8 |  |  |  | 0 | 0 | N/A |  | Note: AHU data are considered more accurate than Equipment data;
AHU 9 |  |  |  | 0 | 0 | N/A |  | Equipment Power (heat) is set equal to the resulting AHU Cooling.
AHU 10 |  |  |  | 0 | 0 | N/A
AHU 11 |  |  |  | 0 | 0 | N/A |  | Note: Grayed out data for internal use only.
AHU 12 |  |  |  | 0 | 0 | N/A
AHU 13 |  |  |  | 0 | 0 | N/A
AHU 14 |  |  |  | 0 | 0 | N/A
AHU 15 |  |  |  | 0 | 0 | N/A
AHU 16 |  |  |  | 0 | 0 | N/A
AHU 17 |  |  |  | 0 | 0 | N/A
AHU 18 |  |  |  | 0 | 0 | N/A
AHU 19 |  |  |  | 0 | 0 | N/A
AHU 20 |  |  |  | 0 | 0 | N/A
AHU 21 |  |  |  | 0 | 0 | N/A
AHU 22 |  |  |  | 0 | 0 | N/A
AHU 23 |  |  |  | 0 | 0 | N/A
AHU 24 |  |  |  | 0 | 0 | N/A
AHU 25 |  |  |  | 0 | 0 | N/A
AHU 26 |  |  |  | 0 | 0 | N/A
AHU 27 |  |  |  | 0 | 0 | N/A
AHU 28 |  |  |  | 0 | 0 | N/A
AHU 29 |  |  |  | 0 | 0 | N/A
AHU 30 |  |  |  | 0 | 0 | N/A
AHU 31 |  |  |  | 0 | 0 | N/A
AHU 32 |  |  |  | 0 | 0 | N/A
AHU 33 |  |  |  | 0 | 0 | N/A
AHU 34 |  |  |  | 0 | 0 | N/A
AHU 35 |  |  |  | 0 | 0 | N/A
AHU 36 |  |  |  | 0 | 0 | N/A
AHU 37 |  |  |  | 0 | 0 | N/A
AHU 38 |  |  |  | 0 | 0 | N/A
AHU 39 |  |  |  | 0 | 0 | N/A
AHU 40 |  |  |  | 0 | 0 | N/A
Sum | 30000 | 0 |  | 65 | 78.3333 | 13.3333
| Total | Max-Min |  | Typical (airflow weighted) |  | Typical (airflow weighted)
| AHU | AHU supply |  | AHU supply air |  | AHU
| airflow | temperature |  | temperature |  | temperature drop
[6 empty] | 126.595 | AHU kW Cooling
2
[6 empty] | 35.9645 | AHU Ton Cooling
AHU Count
Resulting
AHU Cooling

## Step 2 Equip
Step 2: EQUIPMENT
Select Class Option: |  | Similar DT(P) | [6 empty] | By inserting the requested equipment data (yellow cells), this spreadsheet
[5 empty] | V | DT | DT |  | will calculate two pieces of data (orange boxes) and insert them on the
| Measured | Estimated | Number of | Estimated | Tot Class | Airflow |  |  | Main Input (Step 4) sheet. "Equipment" includes heat-generating electronic
| Rise (DT) | Airflow (V) | Units (U) | Airflow (V) | Airflow | Fraction |  |  | equipment (IT) as well as electric equipment such as PDU and UPS.
Class | [F] or [C] | [cfm] or [m3/s] | [-] | [cfm] or [m3/s] | [cfm] or [m3/s] | [-] | DTw
1 | 10 | 100 | 10 | 1000 | 1000 | 0.1 | 1 |  | The principal purpose of the data transfer is to help calculate the Return
2 | 15 | 200 | 0 | 0 | 0 | 0 | 0 |  | Temperature Index (RTI)TM on the Main Input sheet. This index plays
3 | 20 | 300 | 0 | 0 | 0 | 0 | 0 |  | an important role in understanding whether the data center is over-
4 | 25 | 400 | 8 | 2000 | 3200 | 0.2 | 5 |  | (by-pass) or under (recirculation) ventilated.
5 | 30 | 500 | 8 | 4000 | 4000 | 0.4 | 12
6 | 35 | 600 | 5 | 3000 | 3000 | 0.3 | 10.5 |  | Three options are available through the "Select Class Option" box:
7 |  |  |  |  | 0 | 0 | 0
8 |  |  |  |  | 0 | 0 | 0 |  | Similar DT: "Class" refers to equipment with similar measured temperature rise (DT);
9 |  |  |  |  | 0 | 0 | 0 |  |  | used with corresponding fair estimates of airflow (V).
10 |  |  |  |  | 0 | 0 | 0 |  | Similar V: "Class" refers to equipment with similar estimated airflow (V);
used with corresponding number of units (U).
|  |  |  | 10000 |  |  | 27.5892 | F or C | Similar DT(P): "Class" refers to equipment with similar measured temperature rise (DT);
|  |  |  | Total |  |  | Typical (airflow weighted) equipment temperature rise |  |  | used with corresponding measured power (P).
|  |  | DT-P |  |  |  | "Similar DT": Based on yellow cells.
| Measured | Measured | Tot Class |  |  |  | 14498.424 | cfm or m3/s | Group the equipment into Classes with similar temperature rise (DT) or
| Rise (DT) | Power (P) | Airflow |  |  | Total equipment airflow |  |  | airflow rates (V) and fill in the remaining information (yellow cells).
Class | [F] or [C] | [W] | [cfm] or [m3/s] |  |  |  | "Similar V" or "Similar DT(P)": Based on yellow cells.
1 | 10 | 10000 | 3159.6815 | [5 empty] | Tip: "Class" can be on server level, rack-level, or any spatial level defined
2 | 15 | 0 | 0 |  |  |  | 126.595 | kW | by the user.
3 | 20 | 0 | 0 |  |  |  | Equipment power (= AHU cooling)
4 | 25 | 24000 | 3033.2942 |  |  | Compare with UPS readings if available. |  |  | Tip: If no data are available, select "Similar DT" and fill in one row only.
5 | 30 | 48000 | 5055.4903 |  |  | If poor agreement, revisit Steps 1 and 2, |  |  | Estimate DT (table below may help) and set Airflow to any positive number.
6 | 35 | 36000 | 3249.9581 |  |  |  | looking for potential errors.
7 | [8 empty] | Equipment Mix |  | DT [F] | DT [C]
8 | [8 empty] | Mainly traditional equipment |  | 10 to 20 | 6 to 11
9 | [8 empty] | Mainly modern equipment |  | 20 to 30 | 11 to 17
10 | [8 empty] | Mainly blade equipment |  | 30 to 50 | 17 to 28
|  | 118 | kW |  |  |  | Power imbalance |  | Note: Grayed out data for internal use only.
|  | Total measured power |  |  |  |  | (Between cells H27 and C37)
|  | Compare with Equipment power (white box). |  |  |  |  | 6.7894 | %
If poor agreement, revisit Steps 1 and 2 to avoid large
errors in total equipment airflow and temperature rise.
Poor agreement will not affect Equipment power.

## Step 3 RCI
Step 3: RCI
# | Intake Temp [F] or [C] |  |  |  | By inserting the IT equipment intake temperatures (yellow cells), this spreadsheet
1 | 58 |  | 0 | 7 | will calculate the Rack Cooling Index (RCI)Ò and insert RCI(HI) and RCI(LO) on the
2 | 72 |  | 0 | 0 | Main Input (Step 4) sheet.
3 | 68 |  | 0 | 0
4 | 62 |  | 0 | 3 | This index plays an important role in understanding whether the data center is
5 | 81 |  | 1 | 0 | complying with the recommended and allowable intake temperature ranges
6 | 65 |  | 0 | 0 | as specified in Table B on the next spreadsheet (Step 4 Main Input).
7 | 56 |  | 0 | 9
8 | 71 |  | 0 | 0 | Note: Max 999 IT equipment intake temperatures, insert from top down.
9 | 65 |  | 0 | 0
10 | 68 |  | 0 | 0 | Tip: If no data are available, leave all yellow input cells blank.
11 | 60 |  | 0 | 5
12 | 69 |  | 0 | 0 | Note: Grayed out data for internal use only.
13 | 62 |  | 0 | 3
14 | 73 |  | 0 | 0
15 | 64 |  | 0 | 1
16 | 65 |  | 0 | 0
17 | 58 |  | 0 | 7 |  | Rack Cooling Index (RCI): Ideal=100%, Poor (often considered) <90%
18 | 67 |  | 0 | 0
19 | 58 |  | 0 | 7 |  | RCIHI
20 | 69 |  | 0 | 0 |  | 99.5 | % | ("*" means at least one intake > max allowable)
21 |  |  | 0 | 0
22 |  |  | 0 | 0
23 |  |  | 0 | 0 |  | RCILO
24 |  |  | 0 | 0 |  | 65 | * % | ("*" means at least one intake < min allowable)
25 |  |  | 0 | 0 |  | Poor
26 |  |  | 0 | 0 |  | RCI is based on the following recommended and allowable ranges
27 |  |  | 0 | 0 |  | (specified in Step 4 under "Current" for Questions 1 and 2 in Table B):
28 |  |  | 0 | 0
29 |  |  | 0 | 0 |  |  |  | Min | Max
30 |  |  | 0 | 0 |  | Recommended |  | 65 | 80
31 |  |  | 0 | 0 |  | Allowable |  | 59 | 90
32 |  |  | 0 | 0
33 |  |  | 0 | 0
34 |  |  | 0 | 0
35 |  |  | 0 | 0
36 |  |  | 0 | 0
37 |  |  | 0 | 0
38 |  |  | 0 | 0
39 |  |  | 0 | 0
40 |  |  | 0 | 0
41 |  |  | 0 | 0
42 |  |  | 0 | 0
43 |  |  | 0 | 0
44 |  |  | 0 | 0
45 |  |  | 0 | 0
46 |  |  | 0 | 0
47 |  |  | 0 | 0
48 |  |  | 0 | 0
49 |  |  | 0 | 0
50 |  |  | 0 | 0
51 |  |  | 0 | 0
52 |  |  | 0 | 0
53 |  |  | 0 | 0
54 |  |  | 0 | 0
55 |  |  | 0 | 0
56 |  |  | 0 | 0
57 |  |  | 0 | 0
58 |  |  | 0 | 0
59 |  |  | 0 | 0
60 |  |  | 0 | 0
61 |  |  | 0 | 0
62 |  |  | 0 | 0
63 |  |  | 0 | 0
64 |  |  | 0 | 0
65 |  |  | 0 | 0
66 |  |  | 0 | 0
67 |  |  | 0 | 0
68 |  |  | 0 | 0
69 |  |  | 0 | 0
70 |  |  | 0 | 0
71 |  |  | 0 | 0
72 |  |  | 0 | 0
73 |  |  | 0 | 0
74 |  |  | 0 | 0
75 |  |  | 0 | 0
76 |  |  | 0 | 0
77 |  |  | 0 | 0
78 |  |  | 0 | 0
79 |  |  | 0 | 0
80 |  |  | 0 | 0
81 |  |  | 0 | 0
82 |  |  | 0 | 0
83 |  |  | 0 | 0
84 |  |  | 0 | 0
85 |  |  | 0 | 0
86 |  |  | 0 | 0
87 |  |  | 0 | 0
88 |  |  | 0 | 0
89 |  |  | 0 | 0
90 |  |  | 0 | 0
91 |  |  | 0 | 0
92 |  |  | 0 | 0
93 |  |  | 0 | 0
94 |  |  | 0 | 0
95 |  |  | 0 | 0
96 |  |  | 0 | 0
97 |  |  | 0 | 0
98 |  |  | 0 | 0
99 |  |  | 0 | 0
100 |  |  | 0 | 0
101 |  |  | 0 | 0
102 |  |  | 0 | 0
103 |  |  | 0 | 0
104 |  |  | 0 | 0
105 |  |  | 0 | 0
106 |  |  | 0 | 0
107 |  |  | 0 | 0
108 |  |  | 0 | 0
109 |  |  | 0 | 0
110 |  |  | 0 | 0
111 |  |  | 0 | 0
112 |  |  | 0 | 0
113 |  |  | 0 | 0
114 |  |  | 0 | 0
115 |  |  | 0 | 0
116 |  |  | 0 | 0
117 |  |  | 0 | 0
118 |  |  | 0 | 0
119 |  |  | 0 | 0
120 |  |  | 0 | 0
121 |  |  | 0 | 0
122 |  |  | 0 | 0
123 |  |  | 0 | 0
124 |  |  | 0 | 0
125 |  |  | 0 | 0
126 |  |  | 0 | 0
127 |  |  | 0 | 0
128 |  |  | 0 | 0
129 |  |  | 0 | 0
130 |  |  | 0 | 0
131 |  |  | 0 | 0
132 |  |  | 0 | 0
133 |  |  | 0 | 0
134 |  |  | 0 | 0
135 |  |  | 0 | 0
136 |  |  | 0 | 0
137 |  |  | 0 | 0
138 |  |  | 0 | 0
139 |  |  | 0 | 0
140 |  |  | 0 | 0
141 |  |  | 0 | 0
142 |  |  | 0 | 0
143 |  |  | 0 | 0
144 |  |  | 0 | 0
145 |  |  | 0 | 0
146 |  |  | 0 | 0
147 |  |  | 0 | 0
148 |  |  | 0 | 0
149 |  |  | 0 | 0
150 |  |  | 0 | 0
151 |  |  | 0 | 0
152 |  |  | 0 | 0
153 |  |  | 0 | 0
154 |  |  | 0 | 0
155 |  |  | 0 | 0
156 |  |  | 0 | 0
157 |  |  | 0 | 0
158 |  |  | 0 | 0
159 |  |  | 0 | 0
160 |  |  | 0 | 0
161 |  |  | 0 | 0
162 |  |  | 0 | 0
163 |  |  | 0 | 0
164 |  |  | 0 | 0
165 |  |  | 0 | 0
166 |  |  | 0 | 0
167 |  |  | 0 | 0
168 |  |  | 0 | 0
169 |  |  | 0 | 0
170 |  |  | 0 | 0
171 |  |  | 0 | 0
172 |  |  | 0 | 0
173 |  |  | 0 | 0
174 |  |  | 0 | 0
175 |  |  | 0 | 0
176 |  |  | 0 | 0
177 |  |  | 0 | 0
178 |  |  | 0 | 0
179 |  |  | 0 | 0
180 |  |  | 0 | 0
181 |  |  | 0 | 0
182 |  |  | 0 | 0
183 |  |  | 0 | 0
184 |  |  | 0 | 0
185 |  |  | 0 | 0
186 |  |  | 0 | 0
187 |  |  | 0 | 0
188 |  |  | 0 | 0
189 |  |  | 0 | 0
190 |  |  | 0 | 0
191 |  |  | 0 | 0
192 |  |  | 0 | 0
193 |  |  | 0 | 0
194 |  |  | 0 | 0
195 |  |  | 0 | 0
196 |  |  | 0 | 0
197 |  |  | 0 | 0
198 |  |  | 0 | 0
199 |  |  | 0 | 0
200 |  |  | 0 | 0
201 |  |  | 0 | 0
202 |  |  | 0 | 0
203 |  |  | 0 | 0
204 |  |  | 0 | 0
205 |  |  | 0 | 0
206 |  |  | 0 | 0
207 |  |  | 0 | 0
208 |  |  | 0 | 0
209 |  |  | 0 | 0
210 |  |  | 0 | 0
211 |  |  | 0 | 0
212 |  |  | 0 | 0
213 |  |  | 0 | 0
214 |  |  | 0 | 0
215 |  |  | 0 | 0
216 |  |  | 0 | 0
217 |  |  | 0 | 0
218 |  |  | 0 | 0
219 |  |  | 0 | 0
220 |  |  | 0 | 0
221 |  |  | 0 | 0
222 |  |  | 0 | 0
223 |  |  | 0 | 0
224 |  |  | 0 | 0
225 |  |  | 0 | 0
226 |  |  | 0 | 0
227 |  |  | 0 | 0
228 |  |  | 0 | 0
229 |  |  | 0 | 0
230 |  |  | 0 | 0
231 |  |  | 0 | 0
232 |  |  | 0 | 0
233 |  |  | 0 | 0
234 |  |  | 0 | 0
235 |  |  | 0 | 0
236 |  |  | 0 | 0
237 |  |  | 0 | 0
238 |  |  | 0 | 0
239 |  |  | 0 | 0
240 |  |  | 0 | 0
241 |  |  | 0 | 0
242 |  |  | 0 | 0
243 |  |  | 0 | 0
244 |  |  | 0 | 0
245 |  |  | 0 | 0
246 |  |  | 0 | 0
247 |  |  | 0 | 0
248 |  |  | 0 | 0
249 |  |  | 0 | 0
250 |  |  | 0 | 0
251 |  |  | 0 | 0
252 |  |  | 0 | 0
253 |  |  | 0 | 0
254 |  |  | 0 | 0
255 |  |  | 0 | 0
256 |  |  | 0 | 0
257 |  |  | 0 | 0
258 |  |  | 0 | 0
259 |  |  | 0 | 0
260 |  |  | 0 | 0
261 |  |  | 0 | 0
262 |  |  | 0 | 0
263 |  |  | 0 | 0
264 |  |  | 0 | 0
265 |  |  | 0 | 0
266 |  |  | 0 | 0
267 |  |  | 0 | 0
268 |  |  | 0 | 0
269 |  |  | 0 | 0
270 |  |  | 0 | 0
271 |  |  | 0 | 0
272 |  |  | 0 | 0
273 |  |  | 0 | 0
274 |  |  | 0 | 0
275 |  |  | 0 | 0
276 |  |  | 0 | 0
277 |  |  | 0 | 0
278 |  |  | 0 | 0
279 |  |  | 0 | 0
280 |  |  | 0 | 0
281 |  |  | 0 | 0
282 |  |  | 0 | 0
283 |  |  | 0 | 0
284 |  |  | 0 | 0
285 |  |  | 0 | 0
286 |  |  | 0 | 0
287 |  |  | 0 | 0
288 |  |  | 0 | 0
289 |  |  | 0 | 0
290 |  |  | 0 | 0
291 |  |  | 0 | 0
292 |  |  | 0 | 0
293 |  |  | 0 | 0
294 |  |  | 0 | 0
295 |  |  | 0 | 0
296 |  |  | 0 | 0
297 |  |  | 0 | 0
298 |  |  | 0 | 0
299 |  |  | 0 | 0
300 |  |  | 0 | 0
301 |  |  | 0 | 0
302 |  |  | 0 | 0
303 |  |  | 0 | 0
304 |  |  | 0 | 0
305 |  |  | 0 | 0
306 |  |  | 0 | 0
307 |  |  | 0 | 0
308 |  |  | 0 | 0
309 |  |  | 0 | 0
310 |  |  | 0 | 0
311 |  |  | 0 | 0
312 |  |  | 0 | 0
313 |  |  | 0 | 0
314 |  |  | 0 | 0
315 |  |  | 0 | 0
316 |  |  | 0 | 0
317 |  |  | 0 | 0
318 |  |  | 0 | 0
319 |  |  | 0 | 0
320 |  |  | 0 | 0
321 |  |  | 0 | 0
322 |  |  | 0 | 0
323 |  |  | 0 | 0
324 |  |  | 0 | 0
325 |  |  | 0 | 0
326 |  |  | 0 | 0
327 |  |  | 0 | 0
328 |  |  | 0 | 0
329 |  |  | 0 | 0
330 |  |  | 0 | 0
331 |  |  | 0 | 0
332 |  |  | 0 | 0
333 |  |  | 0 | 0
334 |  |  | 0 | 0
335 |  |  | 0 | 0
336 |  |  | 0 | 0
337 |  |  | 0 | 0
338 |  |  | 0 | 0
339 |  |  | 0 | 0
340 |  |  | 0 | 0
341 |  |  | 0 | 0
342 |  |  | 0 | 0
343 |  |  | 0 | 0
344 |  |  | 0 | 0
345 |  |  | 0 | 0
346 |  |  | 0 | 0
347 |  |  | 0 | 0
348 |  |  | 0 | 0
349 |  |  | 0 | 0
350 |  |  | 0 | 0
351 |  |  | 0 | 0
352 |  |  | 0 | 0
353 |  |  | 0 | 0
354 |  |  | 0 | 0
355 |  |  | 0 | 0
356 |  |  | 0 | 0
357 |  |  | 0 | 0
358 |  |  | 0 | 0
359 |  |  | 0 | 0
360 |  |  | 0 | 0
361 |  |  | 0 | 0
362 |  |  | 0 | 0
363 |  |  | 0 | 0
364 |  |  | 0 | 0
365 |  |  | 0 | 0
366 |  |  | 0 | 0
367 |  |  | 0 | 0
368 |  |  | 0 | 0
369 |  |  | 0 | 0
370 |  |  | 0 | 0
371 |  |  | 0 | 0
372 |  |  | 0 | 0
373 |  |  | 0 | 0
374 |  |  | 0 | 0
375 |  |  | 0 | 0
376 |  |  | 0 | 0
377 |  |  | 0 | 0
378 |  |  | 0 | 0
379 |  |  | 0 | 0
380 |  |  | 0 | 0
381 |  |  | 0 | 0
382 |  |  | 0 | 0
383 |  |  | 0 | 0
384 |  |  | 0 | 0
385 |  |  | 0 | 0
386 |  |  | 0 | 0
387 |  |  | 0 | 0
388 |  |  | 0 | 0
389 |  |  | 0 | 0
390 |  |  | 0 | 0
391 |  |  | 0 | 0
392 |  |  | 0 | 0
393 |  |  | 0 | 0
394 |  |  | 0 | 0
395 |  |  | 0 | 0
396 |  |  | 0 | 0
397 |  |  | 0 | 0
398 |  |  | 0 | 0
399 |  |  | 0 | 0
400 |  |  | 0 | 0
401 |  |  | 0 | 0
402 |  |  | 0 | 0
403 |  |  | 0 | 0
404 |  |  | 0 | 0
405 |  |  | 0 | 0
406 |  |  | 0 | 0
407 |  |  | 0 | 0
408 |  |  | 0 | 0
409 |  |  | 0 | 0
410 |  |  | 0 | 0
411 |  |  | 0 | 0
412 |  |  | 0 | 0
413 |  |  | 0 | 0
414 |  |  | 0 | 0
415 |  |  | 0 | 0
416 |  |  | 0 | 0
417 |  |  | 0 | 0
418 |  |  | 0 | 0
419 |  |  | 0 | 0
420 |  |  | 0 | 0
421 |  |  | 0 | 0
422 |  |  | 0 | 0
423 |  |  | 0 | 0
424 |  |  | 0 | 0
425 |  |  | 0 | 0
426 |  |  | 0 | 0
427 |  |  | 0 | 0
428 |  |  | 0 | 0
429 |  |  | 0 | 0
430 |  |  | 0 | 0
431 |  |  | 0 | 0
432 |  |  | 0 | 0
433 |  |  | 0 | 0
434 |  |  | 0 | 0
435 |  |  | 0 | 0
436 |  |  | 0 | 0
437 |  |  | 0 | 0
438 |  |  | 0 | 0
439 |  |  | 0 | 0
440 |  |  | 0 | 0
441 |  |  | 0 | 0
442 |  |  | 0 | 0
443 |  |  | 0 | 0
444 |  |  | 0 | 0
445 |  |  | 0 | 0
446 |  |  | 0 | 0
447 |  |  | 0 | 0
448 |  |  | 0 | 0
449 |  |  | 0 | 0
450 |  |  | 0 | 0
451 |  |  | 0 | 0
452 |  |  | 0 | 0
453 |  |  | 0 | 0
454 |  |  | 0 | 0
455 |  |  | 0 | 0
456 |  |  | 0 | 0
457 |  |  | 0 | 0
458 |  |  | 0 | 0
459 |  |  | 0 | 0
460 |  |  | 0 | 0
461 |  |  | 0 | 0
462 |  |  | 0 | 0
463 |  |  | 0 | 0
464 |  |  | 0 | 0
465 |  |  | 0 | 0
466 |  |  | 0 | 0
467 |  |  | 0 | 0
468 |  |  | 0 | 0
469 |  |  | 0 | 0
470 |  |  | 0 | 0
471 |  |  | 0 | 0
472 |  |  | 0 | 0
473 |  |  | 0 | 0
474 |  |  | 0 | 0
475 |  |  | 0 | 0
476 |  |  | 0 | 0
477 |  |  | 0 | 0
478 |  |  | 0 | 0
479 |  |  | 0 | 0
480 |  |  | 0 | 0
481 |  |  | 0 | 0
482 |  |  | 0 | 0
483 |  |  | 0 | 0
484 |  |  | 0 | 0
485 |  |  | 0 | 0
486 |  |  | 0 | 0
487 |  |  | 0 | 0
488 |  |  | 0 | 0
489 |  |  | 0 | 0
490 |  |  | 0 | 0
491 |  |  | 0 | 0
492 |  |  | 0 | 0
493 |  |  | 0 | 0
494 |  |  | 0 | 0
495 |  |  | 0 | 0
496 |  |  | 0 | 0
497 |  |  | 0 | 0
498 |  |  | 0 | 0
499 |  |  | 0 | 0
500 |  |  | 0 | 0
501 |  |  | 0 | 0
502 |  |  | 0 | 0
503 |  |  | 0 | 0
504 |  |  | 0 | 0
505 |  |  | 0 | 0
506 |  |  | 0 | 0
507 |  |  | 0 | 0
508 |  |  | 0 | 0
509 |  |  | 0 | 0
510 |  |  | 0 | 0
511 |  |  | 0 | 0
512 |  |  | 0 | 0
513 |  |  | 0 | 0
514 |  |  | 0 | 0
515 |  |  | 0 | 0
516 |  |  | 0 | 0
517 |  |  | 0 | 0
518 |  |  | 0 | 0
519 |  |  | 0 | 0
520 |  |  | 0 | 0
521 |  |  | 0 | 0
522 |  |  | 0 | 0
523 |  |  | 0 | 0
524 |  |  | 0 | 0
525 |  |  | 0 | 0
526 |  |  | 0 | 0
527 |  |  | 0 | 0
528 |  |  | 0 | 0
529 |  |  | 0 | 0
530 |  |  | 0 | 0
531 |  |  | 0 | 0
532 |  |  | 0 | 0
533 |  |  | 0 | 0
534 |  |  | 0 | 0
535 |  |  | 0 | 0
536 |  |  | 0 | 0
537 |  |  | 0 | 0
538 |  |  | 0 | 0
539 |  |  | 0 | 0
540 |  |  | 0 | 0
541 |  |  | 0 | 0
542 |  |  | 0 | 0
543 |  |  | 0 | 0
544 |  |  | 0 | 0
545 |  |  | 0 | 0
546 |  |  | 0 | 0
547 |  |  | 0 | 0
548 |  |  | 0 | 0
549 |  |  | 0 | 0
550 |  |  | 0 | 0
551 |  |  | 0 | 0
552 |  |  | 0 | 0
553 |  |  | 0 | 0
554 |  |  | 0 | 0
555 |  |  | 0 | 0
556 |  |  | 0 | 0
557 |  |  | 0 | 0
558 |  |  | 0 | 0
559 |  |  | 0 | 0
560 |  |  | 0 | 0
561 |  |  | 0 | 0
562 |  |  | 0 | 0
563 |  |  | 0 | 0
564 |  |  | 0 | 0
565 |  |  | 0 | 0
566 |  |  | 0 | 0
567 |  |  | 0 | 0
568 |  |  | 0 | 0
569 |  |  | 0 | 0
570 |  |  | 0 | 0
571 |  |  | 0 | 0
572 |  |  | 0 | 0
573 |  |  | 0 | 0
574 |  |  | 0 | 0
575 |  |  | 0 | 0
576 |  |  | 0 | 0
577 |  |  | 0 | 0
578 |  |  | 0 | 0
579 |  |  | 0 | 0
580 |  |  | 0 | 0
581 |  |  | 0 | 0
582 |  |  | 0 | 0
583 |  |  | 0 | 0
584 |  |  | 0 | 0
585 |  |  | 0 | 0
586 |  |  | 0 | 0
587 |  |  | 0 | 0
588 |  |  | 0 | 0
589 |  |  | 0 | 0
590 |  |  | 0 | 0
591 |  |  | 0 | 0
592 |  |  | 0 | 0
593 |  |  | 0 | 0
594 |  |  | 0 | 0
595 |  |  | 0 | 0
596 |  |  | 0 | 0
597 |  |  | 0 | 0
598 |  |  | 0 | 0
599 |  |  | 0 | 0
600 |  |  | 0 | 0
601 |  |  | 0 | 0
602 |  |  | 0 | 0
603 |  |  | 0 | 0
604 |  |  | 0 | 0
605 |  |  | 0 | 0
606 |  |  | 0 | 0
607 |  |  | 0 | 0
608 |  |  | 0 | 0
609 |  |  | 0 | 0
610 |  |  | 0 | 0
611 |  |  | 0 | 0
612 |  |  | 0 | 0
613 |  |  | 0 | 0
614 |  |  | 0 | 0
615 |  |  | 0 | 0
616 |  |  | 0 | 0
617 |  |  | 0 | 0
618 |  |  | 0 | 0
619 |  |  | 0 | 0
620 |  |  | 0 | 0
621 |  |  | 0 | 0
622 |  |  | 0 | 0
623 |  |  | 0 | 0
624 |  |  | 0 | 0
625 |  |  | 0 | 0
626 |  |  | 0 | 0
627 |  |  | 0 | 0
628 |  |  | 0 | 0
629 |  |  | 0 | 0
630 |  |  | 0 | 0
631 |  |  | 0 | 0
632 |  |  | 0 | 0
633 |  |  | 0 | 0
634 |  |  | 0 | 0
635 |  |  | 0 | 0
636 |  |  | 0 | 0
637 |  |  | 0 | 0
638 |  |  | 0 | 0
639 |  |  | 0 | 0
640 |  |  | 0 | 0
641 |  |  | 0 | 0
642 |  |  | 0 | 0
643 |  |  | 0 | 0
644 |  |  | 0 | 0
645 |  |  | 0 | 0
646 |  |  | 0 | 0
647 |  |  | 0 | 0
648 |  |  | 0 | 0
649 |  |  | 0 | 0
650 |  |  | 0 | 0
651 |  |  | 0 | 0
652 |  |  | 0 | 0
653 |  |  | 0 | 0
654 |  |  | 0 | 0
655 |  |  | 0 | 0
656 |  |  | 0 | 0
657 |  |  | 0 | 0
658 |  |  | 0 | 0
659 |  |  | 0 | 0
660 |  |  | 0 | 0
661 |  |  | 0 | 0
662 |  |  | 0 | 0
663 |  |  | 0 | 0
664 |  |  | 0 | 0
665 |  |  | 0 | 0
666 |  |  | 0 | 0
667 |  |  | 0 | 0
668 |  |  | 0 | 0
669 |  |  | 0 | 0
670 |  |  | 0 | 0
671 |  |  | 0 | 0
672 |  |  | 0 | 0
673 |  |  | 0 | 0
674 |  |  | 0 | 0
675 |  |  | 0 | 0
676 |  |  | 0 | 0
677 |  |  | 0 | 0
678 |  |  | 0 | 0
679 |  |  | 0 | 0
680 |  |  | 0 | 0
681 |  |  | 0 | 0
682 |  |  | 0 | 0
683 |  |  | 0 | 0
684 |  |  | 0 | 0
685 |  |  | 0 | 0
686 |  |  | 0 | 0
687 |  |  | 0 | 0
688 |  |  | 0 | 0
689 |  |  | 0 | 0
690 |  |  | 0 | 0
691 |  |  | 0 | 0
692 |  |  | 0 | 0
693 |  |  | 0 | 0
694 |  |  | 0 | 0
695 |  |  | 0 | 0
696 |  |  | 0 | 0
697 |  |  | 0 | 0
698 |  |  | 0 | 0
699 |  |  | 0 | 0
700 |  |  | 0 | 0
701 |  |  | 0 | 0
702 |  |  | 0 | 0
703 |  |  | 0 | 0
704 |  |  | 0 | 0
705 |  |  | 0 | 0
706 |  |  | 0 | 0
707 |  |  | 0 | 0
708 |  |  | 0 | 0
709 |  |  | 0 | 0
710 |  |  | 0 | 0
711 |  |  | 0 | 0
712 |  |  | 0 | 0
713 |  |  | 0 | 0
714 |  |  | 0 | 0
715 |  |  | 0 | 0
716 |  |  | 0 | 0
717 |  |  | 0 | 0
718 |  |  | 0 | 0
719 |  |  | 0 | 0
720 |  |  | 0 | 0
721 |  |  | 0 | 0
722 |  |  | 0 | 0
723 |  |  | 0 | 0
724 |  |  | 0 | 0
725 |  |  | 0 | 0
726 |  |  | 0 | 0
727 |  |  | 0 | 0
728 |  |  | 0 | 0
729 |  |  | 0 | 0
730 |  |  | 0 | 0
731 |  |  | 0 | 0
732 |  |  | 0 | 0
733 |  |  | 0 | 0
734 |  |  | 0 | 0
735 |  |  | 0 | 0
736 |  |  | 0 | 0
737 |  |  | 0 | 0
738 |  |  | 0 | 0
739 |  |  | 0 | 0
740 |  |  | 0 | 0
741 |  |  | 0 | 0
742 |  |  | 0 | 0
743 |  |  | 0 | 0
744 |  |  | 0 | 0
745 |  |  | 0 | 0
746 |  |  | 0 | 0
747 |  |  | 0 | 0
748 |  |  | 0 | 0
749 |  |  | 0 | 0
750 |  |  | 0 | 0
751 |  |  | 0 | 0
752 |  |  | 0 | 0
753 |  |  | 0 | 0
754 |  |  | 0 | 0
755 |  |  | 0 | 0
756 |  |  | 0 | 0
757 |  |  | 0 | 0
758 |  |  | 0 | 0
759 |  |  | 0 | 0
760 |  |  | 0 | 0
761 |  |  | 0 | 0
762 |  |  | 0 | 0
763 |  |  | 0 | 0
764 |  |  | 0 | 0
765 |  |  | 0 | 0
766 |  |  | 0 | 0
767 |  |  | 0 | 0
768 |  |  | 0 | 0
769 |  |  | 0 | 0
770 |  |  | 0 | 0
771 |  |  | 0 | 0
772 |  |  | 0 | 0
773 |  |  | 0 | 0
774 |  |  | 0 | 0
775 |  |  | 0 | 0
776 |  |  | 0 | 0
777 |  |  | 0 | 0
778 |  |  | 0 | 0
779 |  |  | 0 | 0
780 |  |  | 0 | 0
781 |  |  | 0 | 0
782 |  |  | 0 | 0
783 |  |  | 0 | 0
784 |  |  | 0 | 0
785 |  |  | 0 | 0
786 |  |  | 0 | 0
787 |  |  | 0 | 0
788 |  |  | 0 | 0
789 |  |  | 0 | 0
790 |  |  | 0 | 0
791 |  |  | 0 | 0
792 |  |  | 0 | 0
793 |  |  | 0 | 0
794 |  |  | 0 | 0
795 |  |  | 0 | 0
796 |  |  | 0 | 0
797 |  |  | 0 | 0
798 |  |  | 0 | 0
799 |  |  | 0 | 0
800 |  |  | 0 | 0
801 |  |  | 0 | 0
802 |  |  | 0 | 0
803 |  |  | 0 | 0
804 |  |  | 0 | 0
805 |  |  | 0 | 0
806 |  |  | 0 | 0
807 |  |  | 0 | 0
808 |  |  | 0 | 0
809 |  |  | 0 | 0
810 |  |  | 0 | 0
811 |  |  | 0 | 0
812 |  |  | 0 | 0
813 |  |  | 0 | 0
814 |  |  | 0 | 0
815 |  |  | 0 | 0
816 |  |  | 0 | 0
817 |  |  | 0 | 0
818 |  |  | 0 | 0
819 |  |  | 0 | 0
820 |  |  | 0 | 0
821 |  |  | 0 | 0
822 |  |  | 0 | 0
823 |  |  | 0 | 0
824 |  |  | 0 | 0
825 |  |  | 0 | 0
826 |  |  | 0 | 0
827 |  |  | 0 | 0
828 |  |  | 0 | 0
829 |  |  | 0 | 0
830 |  |  | 0 | 0
831 |  |  | 0 | 0
832 |  |  | 0 | 0
833 |  |  | 0 | 0
834 |  |  | 0 | 0
835 |  |  | 0 | 0
836 |  |  | 0 | 0
837 |  |  | 0 | 0
838 |  |  | 0 | 0
839 |  |  | 0 | 0
840 |  |  | 0 | 0
841 |  |  | 0 | 0
842 |  |  | 0 | 0
843 |  |  | 0 | 0
844 |  |  | 0 | 0
845 |  |  | 0 | 0
846 |  |  | 0 | 0
847 |  |  | 0 | 0
848 |  |  | 0 | 0
849 |  |  | 0 | 0
850 |  |  | 0 | 0
851 |  |  | 0 | 0
852 |  |  | 0 | 0
853 |  |  | 0 | 0
854 |  |  | 0 | 0
855 |  |  | 0 | 0
856 |  |  | 0 | 0
857 |  |  | 0 | 0
858 |  |  | 0 | 0
859 |  |  | 0 | 0
860 |  |  | 0 | 0
861 |  |  | 0 | 0
862 |  |  | 0 | 0
863 |  |  | 0 | 0
864 |  |  | 0 | 0
865 |  |  | 0 | 0
866 |  |  | 0 | 0
867 |  |  | 0 | 0
868 |  |  | 0 | 0
869 |  |  | 0 | 0
870 |  |  | 0 | 0
871 |  |  | 0 | 0
872 |  |  | 0 | 0
873 |  |  | 0 | 0
874 |  |  | 0 | 0
875 |  |  | 0 | 0
876 |  |  | 0 | 0
877 |  |  | 0 | 0
878 |  |  | 0 | 0
879 |  |  | 0 | 0
880 |  |  | 0 | 0
881 |  |  | 0 | 0
882 |  |  | 0 | 0
883 |  |  | 0 | 0
884 |  |  | 0 | 0
885 |  |  | 0 | 0
886 |  |  | 0 | 0
887 |  |  | 0 | 0
888 |  |  | 0 | 0
889 |  |  | 0 | 0
890 |  |  | 0 | 0
891 |  |  | 0 | 0
892 |  |  | 0 | 0
893 |  |  | 0 | 0
894 |  |  | 0 | 0
895 |  |  | 0 | 0
896 |  |  | 0 | 0
897 |  |  | 0 | 0
898 |  |  | 0 | 0
899 |  |  | 0 | 0
900 |  |  | 0 | 0
901 |  |  | 0 | 0
902 |  |  | 0 | 0
903 |  |  | 0 | 0
904 |  |  | 0 | 0
905 |  |  | 0 | 0
906 |  |  | 0 | 0
907 |  |  | 0 | 0
908 |  |  | 0 | 0
909 |  |  | 0 | 0
910 |  |  | 0 | 0
911 |  |  | 0 | 0
912 |  |  | 0 | 0
913 |  |  | 0 | 0
914 |  |  | 0 | 0
915 |  |  | 0 | 0
916 |  |  | 0 | 0
917 |  |  | 0 | 0
918 |  |  | 0 | 0
919 |  |  | 0 | 0
920 |  |  | 0 | 0
921 |  |  | 0 | 0
922 |  |  | 0 | 0
923 |  |  | 0 | 0
924 |  |  | 0 | 0
925 |  |  | 0 | 0
926 |  |  | 0 | 0
927 |  |  | 0 | 0
928 |  |  | 0 | 0
929 |  |  | 0 | 0
930 |  |  | 0 | 0
931 |  |  | 0 | 0
932 |  |  | 0 | 0
933 |  |  | 0 | 0
934 |  |  | 0 | 0
935 |  |  | 0 | 0
936 |  |  | 0 | 0
937 |  |  | 0 | 0
938 |  |  | 0 | 0
939 |  |  | 0 | 0
940 |  |  | 0 | 0
941 |  |  | 0 | 0
942 |  |  | 0 | 0
943 |  |  | 0 | 0
944 |  |  | 0 | 0
945 |  |  | 0 | 0
946 |  |  | 0 | 0
947 |  |  | 0 | 0
948 |  |  | 0 | 0
949 |  |  | 0 | 0
950 |  |  | 0 | 0
951 |  |  | 0 | 0
952 |  |  | 0 | 0
953 |  |  | 0 | 0
954 |  |  | 0 | 0
955 |  |  | 0 | 0
956 |  |  | 0 | 0
957 |  |  | 0 | 0
958 |  |  | 0 | 0
959 |  |  | 0 | 0
960 |  |  | 0 | 0
961 |  |  | 0 | 0
962 |  |  | 0 | 0
963 |  |  | 0 | 0
964 |  |  | 0 | 0
965 |  |  | 0 | 0
966 |  |  | 0 | 0
967 |  |  | 0 | 0
968 |  |  | 0 | 0
969 |  |  | 0 | 0
970 |  |  | 0 | 0
971 |  |  | 0 | 0
972 |  |  | 0 | 0
973 |  |  | 0 | 0
974 |  |  | 0 | 0
975 |  |  | 0 | 0
976 |  |  | 0 | 0
977 |  |  | 0 | 0
978 |  |  | 0 | 0
979 |  |  | 0 | 0
980 |  |  | 0 | 0
981 |  |  | 0 | 0
982 |  |  | 0 | 0
983 |  |  | 0 | 0
984 |  |  | 0 | 0
985 |  |  | 0 | 0
986 |  |  | 0 | 0
987 |  |  | 0 | 0
988 |  |  | 0 | 0
989 |  |  | 0 | 0
990 |  |  | 0 | 0
991 |  |  | 0 | 0
992 |  |  | 0 | 0
993 |  |  | 0 | 0
994 |  |  | 0 | 0
995 |  |  | 0 | 0
996 |  |  | 0 | 0
997 |  |  | 0 | 0
998 |  |  | 0 | 0
999 |  |  | 0 | 0
1000 | 72
| 20 |  | 1 | 42
| Count (n) |  | S(HI) | S(LO)
| 81 |  | 10 | 6
| Max |  | Tmaxall-Tmaxrec | Tminrec-Tminall
| 56 | *
Min
65.55
Aver

## Step 4 Main Input
Step 4: MAIN INPUT
Table A: Metrics (Yellow Cells: Enter data, remaining data from the AHU, Equip, and RCI sheets (color coded)).
| Metric |  | Definition | Measured | Unit
| DTAHU |  | Typical (airflow weighted) AHU temperature drop | 13.3333 | F or C |  | Table A: Includes calculated metrics from Steps 1-3 (color coded).
| DTEquip |  | Typical (airflow weighted) equipment temperature rise | 27.5892 | F or C |  | Rack Cooling Index (RCI)Ò: Ideal=100%, Poor (often considered) <90%
| VAHU |  | Total AHU airflow | 30000 | cfm or m3/s |  | Return Temperature Index (RTI)TM: Balanced=100%, By-Pass<100%, Recirc>100%
| VEquip |  | Total equipment airflow | 14498.424 | cfm or m3/s
| RTI |  | Return Temperature Index: DTAHU/DTEquip = VEquip/VAHU (x100) | 48.3281 | % | Over-ventilated | Table B: Questions for Current and Target conditions.
| RCIHI | Alt. 1* | Rack Cooling Index: Measure of absence of over-temperatures | 99.5 | % |  | "Target" refers to realistic Target architecture/controls for raised-floor cooling.
| RCILO | Alt. 1* | Rack Cooling Index: Measure of absence of under-temperatures | 65 | % | Poor Value | Question 1 may reduce chiller energy but increase IT energy by speeding
| IAT max | Alt. 2* | Typical (not extreme) max IT equipment intake temperature | 82 | F or C |  | up the internal cooling fans. The potential energy penalty for the latter is not
| IAT min | Alt. 2* | Typical (not extreme) min IT equipment intake temperature | 58 | F or C |  | included in the Air Management Tool.
| SAT |  | Typical (airflow weighted) AHU supply air temperature | 65 | F or C |  | Questions 3-10 are considered the key factors for Air Management.
| DSAT |  | Maximum difference between AHU supply air temperatures | 0 | F or C
| * Alt. 1 has priority over Alt. 2 | [5 empty] | Note: Grayed out data for internal use only.
Table B: Questions (Yellow cells: Enter data).
| Question |  |  |  |  | Current | Target | Current
|  | Primary Input (impact on Energy estimates--if raised-floor cooling--and recommended Actions) | [5 empty] | L | H
| 1 |  | Recommended IT equipment intake temperature range (statement of reliability) |  |  | ASHRAE/NEBS | Wide | 65 | 80
| 2 |  | Allowable IT equipment intake temperature range (statement of functionality) |  |  | ASHRAE A1 | ASHRAE A2 | 59 | 90
| 3 |  | Aisle containment quality/implementation? |  |  | LOW | HIGH
| 4 |  | Blanking panels in and between racks quality/implementation? |  |  | MID | MID
| 5 |  | Floor leakage quality/implementation (set to "High" if not raised-floor cooling)? |  |  | MID | MID
| 6 |  | Tile/diffuser placement quality/implementation? |  |  | MID | MID
| 7 |  | EC-Class (equipment ventilation protocol) quality/implementation? |  |  | MID | HIGH
| 8 |  | Controls sophistication (CAV/VAV with IAT sensing)? |  |  | LOW | HIGH
| 9 |  | AHU modularity/distribution quality/implementation (set to "High" if not raised-floor cooling)? |  |  | LOW | HIGH
| 10 |  | Cable/pipe management in supply air path quality/implementation? |  |  | LOW | HIGH
Secondary Input (impact on recommended Actions only)
| 11 |  | What is the clear ceiling in feet (or m) (visible floor to visible ceiling)? |  |  | 9
| 12 |  | Is there a dropped ceiling (not necessarily used as airflow plenum)? |  |  | Yes
| 13 |  | Is the IT equipment arranged in straight rows? |  |  | No
| 14 |  | Are there cosmetic doors on the equipment racks? |  |  | Yes
| 15 |  | How many AHUs are operating under normal conditions (exclude stand-by units)? |  |  | 2 | Also Primary Input
| 16 |  | Do some areas have load densities that are ≥ 4 times the average? |  |  | Yes
| 17 |  | Is there any supplemental cooling (liquid and/or air solution)? |  |  | No
| 18 |  | Which is the predominant air supply path? |  |  | Floor Plenum
| 19 |  | Plenum height in feet (or m)? |  |  | 2
| 20 |  | Floor plenum static pressure in in. of water (or Pa)? |  |  | <0.03 (or <7)
| 21 |  |  |  |  | Wide (> 20 deg)
| 22 |  | Which is the predominant air return path? |  |  | Ceiling Plenum
| 23 |  | Ceiling plenum height in feet (or m)? |  |  | 1
| 24 |  | Where are cables/pipes located? |  |  | Floor Plenum
| 25 |  | Central (built-up) or local (CRAC/H) air handling? |  |  | Local on floor
| 26 |  | Do CRAC/H have centralized (networked) or distributed controls? |  |  | Distributed
| 27 |  | Have temperature (and humidity) sensors been calibrated during the past 12 months? |  |  | No
| 28 |  | Is the air-delivery system balanced to ensure correct airflow rates? |  |  | Yes
Management Practices Input (impact on recommended Management Actions only)
| 29 |  | Is there a sensor calibration program in place? |  |  | No
| 30 |  | Is there a floor plenum cable-mining program in place? |  |  | No
| 31 |  | Is there a tile/diffuser-placement program in place? |  |  | No
| 32 |  | Is there a supply plenum-tightness (sealing leaks) program in place? |  |  | No
| 33 |  | Is there a return plenum-tightness (sealing leaks) program in place? |  |  | No
| 34 |  | Is there a rack- and row-tightness (blanking panels) program in place? |  |  | No
| 35 |  | Is there an air-balancing (proper airflow distribution) program in place? |  |  | No

## Step 5 Main Results
Step 5: MAIN RESULTS
Table 1: Numerical output based on user input.
| Table 1: Numerical Output Based on User Input. | [5 empty] | Measured: | With Current architecture/controls (Table B, Questions 1-10)
[7 empty] | Commissioned: | Achievable with Current architecture/controls (Table B, Questions 1 and 3-10)
|  | Measured | Commissioned | Retrofitted | State-of-the-Art |  | Retrofitted: | Achievable with Target architecture/controls (Table B, Questions 1 and 3-10)
| 100/RTI | 2.0692 | 2.0692 | 1.3 | 1 |  | State-of-the-Art: | State-of-the-Art architecture/controls (SAT based on Target recommended range)
| SAT | 65 | 66 | 81 | 83 | F or C
| RAT | 78.3333 | 79.3333 | 102.2225 | 110.5892 | F or C | Note: The "Commissioned" and "Retrofitted" columns valid for raised-floor cooling only.
| RCIHI | 99.5 | % | ("*" means at least one intake > max allowable) |  |  | 100/RTITM = Total AHU Airflow/Total IT Equipment Airflow (VAHU/VEquip)
| RCILO | 65 | * % | ("*" means at least one intake < min allowable) |  |  | SAT = Typical (airflow weighted) AHU Supply Air Temperature
| VAHU | 30000 | cfm or m3/s |  |  |  | RAT = Typical (airflow weighted) AHU Return Air Temperature
Table 2: Recommended actions based on user input.
By implementing recommended actions (by revisiting user data input and/or
question responses) further actions may be provided.
Table 2: Recommended Actions Based on User Input.
| # | Actions | [7 empty] | 1.0346 |  | 2 | 1.3
|  | Actions for realizing Commissioned conditions in Table 1 | [6 empty] | #2 | "step" |  | Com VAV | Ret VAV
| 1 | Calibrate Temperature (and Humidity) Sensors
| 2 | N/A | [9 empty] | 2 | 2
| 3 | Extreme Floor Plenum Pressure; Provide Adequate Pressure | [8 empty] | #3 | Min | Min
| 4 | Ensure an Adequate Ratio of IT Equipment Airflow to AHU Airflow | [9 empty] | # Units | # Units
| 5 | N/A | [9 empty] | CAV | CAV
| 6 | N/A
| 7 | N/A | [9 empty] | 2.0692 | 2.0692
| 8 | Supply Air has Under-Temperature for Current Architecture/Controls, See Table 1 | [8 empty] | #4 | Com CAV | Ret CAV
| 9 | Under-Temperatures; Improve Air Management and/or Increase the Supply Air Temperature
| 10 | N/A | [7 empty] | Note: Grayed out data for internal use only.
Actions for realizing Retrofitted or State-of-the-Art conditions in Table 1
| 11 | Network the CRAC/H Controls
| 12 | N/A
| 13 | N/A
| 14 | N/A
| 15 | Shallow Ceiling Plenum; Ensure Match between Heat Load and Plenum Height
| 16 | N/A
| 17 | N/A
| 18 | Remove Abandoned Cables and Other Obstructions from Floor Plenum
| 19 | N/A
| 20 | N/A
| 21 | Convert Supply Fans with Variable Speed Drives (VFD)
| 22 | Configure Equipment in Straight Rows; Prerequisite for Hot and Cold Aisles
| 23 | N/A
| 24 | N/A
| 25 | N/A
| 26 | N/A
| 27 | N/A
| 28 | Use Supplemental Cooling for High-Density Areas
| 29 | Improve CRAC/H Floor Layout
| 30 | N/A
| 31 | Use IT Equipment with Front-to-Rear or Front-to-Top Cooling Airflow (EC-Class)
| 32 | Remove Cosmetic Doors from Equipment Racks or...
| 33 | …Provide Adequate Free Area for Air Movement
| 34 | N/A
| 35 | Implement Equipment Intake Air Temperature Control (program default)
| 36 | N/A
| 37 | N/A
Management Practices
| 38 | Implement a Sensor Calibration Program
| 39 | Implement a Raised-Floor Cable Mining Program
| 40 | Implement a Tile/Diffuser-Placement Program
| 41 | Implement a Plenum-Tightness Program
| 42 | Implement a Rack- and Row-Tightness Program
| 43 | Implement an Air-Balancing Program
| 44 | N/A

## Step 6 Energy Results
Step 6: ENERGY Results (last sheet)
This sheet includes fan and chiller energy, energy costs, carbon emissions, and
[8 empty] | simple payback periods, which can be controlled by twelve yellow input boxes. | [8 empty] | Note: Grayed out data for internal use only.
(All other results can be found on the Main Results sheet, Step 5).
List Row
[8 empty] | Note 1: "Measured" bar is the reference (100%) and values above 100% | [10 empty] | 1
[8 empty] | for other bars will not be displayed. | [8 empty] | Custom | 1.1
[8 empty] | Note 2: The "Commissioned" and "Retrofitted" bars valid for raised-floor cooling only. | [8 empty] | AL | 0.751
[17 empty] | AK | 0.92
| 1/RTI | 2.0692 | 2.0692 | 1.3 | 1 |  |  | Electric Cost: |  | 0.2 | [$/kWh] | [5 empty] | AZ | 0.725
| SAT | 65 | 66 | 81 | 83 | [11 empty] | AR | 1.087 | Arkansas
[17 empty] | CA | 0.479
|  | Measured | Commissioned | Retrofitted | State-of-the-Art | [11 empty] | CO | 1.217
| Fan | 100 | 100 | 24.7987 | 11.2875 |  |  | Fan Exponent: |  | 3 | [-] | (Range: 2 - 3) |  |  |  |  | CT | 0.515
| Chiller | 100 | 98 | 68 | 64 | [11 empty] | DE | 0.868 | Delaware
[8 empty] | For fully turbulent flow there is a cubical (3) relationship between | [8 empty] | FL | 0.834
[8 empty] | fan energy and airflow; for fully laminar flow there is a quadratic (2) | [8 empty] | GA | 0.758
| kWh/yr | 80000 |  | 80000 |  | 19838.9495 | 9030.018 | relationship. For data centers, an exponent of 2.8 is common. | [8 empty] | HI | 1.491 | Hawaii
| $/yr | 16000 |  | 16000 |  | 3967.7899 | 1806.0036 | [9 empty] | ID | 0.271 | Idaho
| lb CO2/yr | 88000 |  | 88000 |  | 21822.8445 | 9933.0198 | kWh/yr (yellow cell far left) = Enter measured annual fan energy. | [8 empty] | IL | 0.653 | Illinois
| SP Yrs |  |  |  |  | 2.0778 | 4.2271 | [5 empty] | Select a State or "Custom" from the drop down |  |  |  | IN | 1.633
[13 empty] | menu. If "Custom" is slected, enter generation CO2 |  |  |  | IA | 0.769 | Iowa
[8 empty] | CO2 Emission Rate: |  | 1.1 | [lbs/kWh] | No SI unit available. | emission rate in yellow box (Range: 0.1-20.0). |  |  |  | KS | 0.838 | Kansas
[8 empty] | (inclluding T&D) | [5 empty] | Select State/Custom | Custom |  | KY | 1.727
[15 empty] | 1.1 | [lbs/kWh] | LA | 0.826
[8 empty] | T&D Losses: |  | 0 | [%] | (Range: 0-10%) |  |  |  |  | ME | 0.301 | Main
[17 empty] | MD | 0.698
[17 empty] | MA | 0.851
[8 empty] | Chiller Factor: |  | 2 | [%/F] or [%/C] | (Range: 1-3 %/F or 2-5 %/C) |  |  |  |  | MI | 1.004
[17 empty] | MN | 0.826
[8 empty] | The chiller energy reduction depends on the supply air temperature | [8 empty] | MS | 0.834 | Mississippi
[8 empty] | as a percentage saving per degree increase. For data center | [8 empty] | MO | 1.636 | Missouri
[8 empty] | applications, a factor between 1 and 3 (I-P) or 2 and 5 (SI) is common. | [8 empty] | MT | 1.045 | Montana
[17 empty] | NE | 1.125 | Nebraska
[8 empty] | Com | Retro | State |  | Com: Commissioned |  |  |  |  | NV | 0.715
[8 empty] | 2000 | 25000 | 60000 | $ - Fan | Retro: Retrofitted |  |  |  |  | NH | 0.304
[8 empty] | 3000 | 95000 | 160000 | $ - Chiller | State: State-of-the-Art |  |  |  |  | NJ | 0.481
[17 empty] | NM | 1.134
| kWh/yr | 350000 |  | 343000 |  | 238000 | 224000 | Implementation Costs attributable to fan and chiller savings, respectively. | [8 empty] | NY | 0.455
| $/yr | 70000 |  | 68600 |  | 47600 | 44800 | Simple Payback (SP) will be calculated based on this input. | [8 empty] | NC | 0.669
| lb CO2/yr | 385000 |  | 377300 |  | 261800 | 246400 | [9 empty] | ND | 1.341
| SP Yrs |  |  | 2.1429 |  | 4.2411 | 6.3492 | kWh/yr (yellow cell far left) = Enter measured annual chiller energy. | [8 empty] | OH | 1.208
| L H2O/yr | ------------------------------------- |  |  | 2217945.1008 | ------------------------------------ | [10 empty] | OK | 0.754
[17 empty] | OR | 0.326
[8 empty] | WUE: |  | 2 | [L/kWh] | (Range: 0-50 L/kWh) |  |  |  |  | PA | 0.726
[17 empty] | RI | 0.833
[8 empty] | WUE depends on type of cooling system. |  |  |  | No IP unit available. |  |  |  |  | SC | 0.567
[17 empty] | SD | 0.303
[17 empty] | TN | 0.698
[17 empty] | TX | 0.856
[17 empty] | UT | 1.561
[17 empty] | VT | 0.036
[17 empty] | VA | 0.599
[17 empty] | WA | 0.202
[17 empty] | WV | 1.944
[17 empty] | WI | 1.267 | Wisconsin
[17 empty] | WY | 1.834

## Lookup (hidden)
LOOKUP |  |  |  | NOTE: Do not enter or change data on this sheet.
Tables show 'achievable' values for raised-floor cooling, VAV fans, and IAT controls.
Calculates TABLE, ROW, and COLUMN numbers based on INPUT sheet (Current and Target)
|  | Current | INDEX | TABLE | ROW | COLUMN | Target | INDEX | TABLE | ROW | COLUMN
1 | Enclosure | LOW | 1 |  | 2 |  | HIGH | 3 |  | 2 |  | Airflow "Blockers"
2 | Panel | MID | 2 |  |  |  | MID | 2
3 | Cutout | MID | 2 |  |  |  | MID | 2 | [6 empty] | Future introduction of weighting factors;
4 | Tiles | MID | 2 |  |  | 2 | MID | 2 |  |  | 3 | Airflow "Drivers" |  |  | presently equal weight for the combined
5 | EC-Class | MID | 2 |  |  |  | HIGH | 3 | [6 empty] | measures.
6 | N/A | N/A | N/A | 1 |  |  | N/A | N/A | 3 |  |  | Airflow "Delivery"
7 | AHU | LOW | 1 |  |  |  | HIGH | 3
8 | Cables | LOW | 1 |  |  |  | HIGH | 3
| Table 1: LOW (INDEX=1) Delivery | [5 empty] | Table 2: MID (INDEX=2) Delivery | [5 empty] | Table 3: HIGH (INDEX=3) Delivery
| COLUMN | 1 | 2 | 3 |  |  | COLUMN | 1 | 2 | 3 |  |  | COLUMN | 1 | 2 | 3
| Lookup for 100/RTI [-] | [5 empty] | Lookup for 100/RTI [-] | [5 empty] | Lookup for 100/RTI [-]
ROW |  | Drivers |  |  |  | ROW |  | Drivers |  |  |  | ROW |  | Drivers
1 | Blockers | 3 | 2.4 | 2 |  | 1 | Blockers | 2.8 | 2.2 | 1.8 |  | 1 | Blockers | 2.6 | 2 | 1.6
2 |  | 2.4 | 2 | 1.7 |  | 2 |  | 2.2 | 1.8 | 1.5 |  | 2 |  | 2 | 1.6 | 1.3
3 |  | 2 | 1.7 | 1.4 |  | 3 |  | 1.8 | 1.5 | 1.2 |  | 3 |  | 1.6 | 1.3 | 1
| COLUMN | 1 | 2 | 3 |  |  | COLUMN | 1 | 2 | 3 |  |  | COLUMN | 1 | 2 | 3
| Lookup for SAT [F] or [C] | [5 empty] | Lookup for SAT [F] or [C] | [5 empty] | Lookup for SAT [F] or [C]
ROW |  | Drivers |  |  |  | ROW |  | Drivers |  |  |  | ROW |  | Drivers
1 | Blockers | 59 | 62 | 64 |  | 1 | Blockers | 63 | 66 | 68 |  | 1 | Blockers | 67 | 70 | 72
2 |  | 62 | 66 | 68 |  | 2 |  | 66 | 70 | 72 |  | 2 |  | 70 | 74 | 76
3 |  | 64 | 68 | 70 |  | 3 |  | 68 | 72 | 74 |  | 3 |  | 72 | 76 | 78
100/RTITM = Total AHU Airflow/Total IT Equipment Airflow (VAHU/VEquip)
SAT = Typical (average) AHU Supply Air Temperature
SAT numbers are based on a recommended intake temperature range of 65-80F or 18-27C (ASHRAE/NEBS); correction will be applied for other intake temperature ranges.

## Action Rules (hidden)
ACTION RULES |  | NOTE: This sheet is not part of the software program;
it shows the rules for the Actions (Table 2, Step 5)
based on user input (Steps 1-4).
|  |  | Question (Table B, Step 4) | [34 empty] | Metrics (Table A, Step 4)
|  |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 1 | 2 | 15 | 17 | 12 | 11 | 18 | 19 | 20 | 32 | 21 | 22 | 23 | 33 | 24 | 30 | 13 | 34 | 31 | 25 | 26 | 16 | 27 | 28 | 35 | 29 | 14 | I | II | III | IV | V | VI | VII | VIII
| Bold items are based on Metrics rather than Questions. |  | Containment | Blanking | Cutout | Tile/Diff | EC-Class | Controls | AHU | Cable | Rec | Allow | #ON | Supp | Dropped | Clear | Supply | F/C-Plenum | F-Plenum | Sealing | Diffuser | Return | C-Plenum | C-Sealing | Cable | Mining | Straight | Tightness | Diff/Tile | Central/Local | Central | Point | Sensor | System | Balance | Calibration | Cosmetic | RTI | RCI(HI) | RCI(LO) | IAT | IAT | Typ | Typ | DTEquip
Action |  |  | Quality | Quality | Quality | Quality | Quality | Quality | dens/dist | Quality | Intake | Intake | AHU | Cooling | Ceiling | Ceiling | Path | Height | Pressure | Program | Charact | Path | Height | Program | Location | Program | Rows | Program | Program | AHU | Controls | Loads | Calibration | Balanced | Program | Program | Doors |  |  |  | Max | Min | SAT | DSAT
44 | EC-001: Calculate metrics RTI and/or RCI | [36 empty] | Blank | Blank | Blank
1 | EC-005: Calibrate Temperature (and Humidity) Sensors | [31 empty] | No
11 | EC-006: Network CRAC/H Controls | [28 empty] | <>Central | Distributed
9 | EC-012: Intake Under-Temperatures | [37 empty] | >90 | <90 | <L | <H
10 | EC-013: Intake Over-Temperatures | [37 empty] | <90 | >90 | >H | >L
2 | EC-014: Align the SAT among the AHU | [42 empty] | >10F (5.6)
12 | EC-015: Intake Over- and Under-Temperatures | [37 empty] | <90 | <90 | >H | <L
38 | EC-016: Implement a Sensor Calibration Program | [34 empty] | No
13 | EC-017: Use wider recommended intake temperature range | [9 empty] | 70-75 (21-24)
14 | AM-001: Shallow Floor Plenum | [15 empty] | F-Plenum | £2 ft (0.61)
15 | AM-002: Shallow Ceiling Plenum | [15 empty] | C-Plenum | £2 ft (0.61) |  |  |  | C-Plenum | £2 ft (0.61)
16 | AM-003: Low Ceiling; Provide Adequate Clear Ceiling | [14 empty] | <9 ft (2.74)
17 | AM-004: Use Existing Dropped Ceiling as Return Plenum | [13 empty] | Yes |  | NOT C-Pl |  |  |  |  | NOT C-Pl
18 | AM-005: Remove Abandoned Cables and Other Obstructions (1) | [8 empty] | Low | [6 empty] | F-Plenum | [7 empty] | F-Plenum
| AM-005: Remove Abandoned Cables and Other Obstructions (2) | [8 empty] | Low | [6 empty] | C-Plenum | [7 empty] | <>F-Plenum
| AM-005: Remove Abandoned Cables and Other Obstructions (3) | [8 empty] | Low | [6 empty] | Overhead | [7 empty] | Overhead
39 | AM-006: Implement a Raised-Floor Cable Mining Program | [15 empty] | F-Plenum | [7 empty] | F-Plenum | No
19 | AM-007: Implement Alternating Hot and Cold Equipment Aisles |  |  |  |  | Low | High | [19 empty] | Yes
20 | AM-008: Provide Physical Separation of Hot and Cold Air |  | Low | <>Low | <>Low | <>Low | High
21 | AM-009: Convert supply fans with Variable Speed Drives (VFD) | [6 empty] | Low
22 | AM-010: Configure Equipment in Straight Rows | [25 empty] | No
23 | AM-011: Place Supply Air Devices in Cold Aisles Only |  |  |  |  | Low | High | [19 empty] | Yes
40 | AM-012: Implement a Tile/Diffuser-Placement Program | [27 empty] | No
24 | AM-013: Use Appropriate Overhead Diffusers | [15 empty] | Duct/Plenum |  |  |  | Wide
25 | AM-014: Place Air Returns at High Elevation | [20 empty] | Free
26 | AM-015: Take Return Air from Hot Aisles |  |  |  |  | Low | High | [14 empty] | <>Free |  |  |  |  | Yes
3 | AM-016: Extreme Floor Plenum Pressure | [15 empty] | F-Plenum |  | <0.03 in. (7) or >0.07 in. (17)
27 | AM-017: Seal Floor Plenum Leaks |  |  |  | Low | [11 empty] | F-Plenum
41 | AM-018: Implement a Plenum-Tightness Program | [15 empty] | F/C-Plenum |  |  | No |  | C-Plenum |  | No
28 | AM-019: Use Supplemental Cooling for high-density areas | [12 empty] | No | [17 empty] | Yes
29 | AM-020: Improve CRAC/H floor layout | [7 empty] | Low | [7 empty] | F-Plenum | [12 empty] | Local on floor
4 | AM-021: Ensure an Adequate Ratio of IT-Equipment to AHU Airflow | [36 empty] | <80, >120
5 | AM-022: Balance the Air Distribution System | [32 empty] | No
30 | AM-023: Use IT Equipment with High Temperature Rise | [43 empty] | <15F (8.3)
31 | AM-024: Use IT Equip with F-R and or F-T Cooling (EC-Class) | [5 empty] | <>High
32 | AM-025: Remove Cosmetic Doors from IT Equipment Racks | [35 empty] | Yes
33 | AM-026: Provide Adequate Free Area on Rack Doors for Air | [35 empty] | Yes
34 | AM-027: Maintain Tight Racks and Unbroken Rows |  |  | Low
42 | AM-028: Implement a Rack- and Row-Tightness Program | [26 empty] | No
6 | AM-030: Explore whether CRAC/H units can be shut OFF | [6 empty] | Low |  |  |  |  | >2 | [16 empty] | <>Central
43 | AM-031: Implement an Air-Balancing Program | [33 empty] | No
7 | AM-042: Over/Under-Ventilated for Current Arch/Cntrl |  | Based on Table 1, Step 5,
8 | AM-043: SA Over/Under-Temperature for Current Arch/Cntrl |  | rather than on Questions/Metrics
35 | AM-044: Implement Equipment Intake Air Temperature Control

## Export (hidden)
Export |  | This sheet provides output for post-processing.
|  |  | Measured | Commissioned | Retrofitted | State-of-the-Art
| Floor Area |  | No Data | No Data | No Data | No Data
| AHU/Rack Power [W] |  | 126595.04 | 126595.04 | 126595.04 | 126595.04
| Average Rack Inlet Temperature [F or C] |  | 65.55 | No Data | No Data | No Data
| Average AHU Temperature drop [F or C] |  | 13.3333 | 13.3333 | 21.2225 | 27.5892
| Average equipment temperature drop [F or C] |  | 27.5892 | 27.5892 | 27.5892 | 27.5892
| Total AHU airflow [cfm or m3/s] |  | 30000 | 30000 | 18847.9513 | 14498.424
| Total equipment airflow [cfm or m3/s] |  | 14498.424 | 14498.424 | 14498.424 | 14498.424
| 100/RTI [-] |  | 2.0692 | 2.0692 | 1.3 | 1
| AHU Supply Temperature [F or C] |  | 65 | 66 | 81 | 83
| AHU Return Temperature [F or C] |  | 78.3333 | 79.3333 | 102.2225 | 110.5892
| Rack Cooling Index (RCIHI) [%] |  | 99.5 | 95 | 95 | 95